## Sheet1
| reported date | status | reported by | reporting chain | issue description | comments/response | communication sent & yet to do | updates needed
1 | 2024-02-21 | open | Luke Hart, IPSA team | Luke to Ian to Pat | 1 - IPS LTDS CIM Factfinder.pdf, as described in: - item 2.1 Busbars and the BusbarGroup - item 2. Line Containment and Circuit - item 2.3 Circuit/Operational Limits - item 2.4 Generation | 1 - IPS LTDS CIM Factfinder response.docx | Verify with IPSA that they got a complete response | none for 2.1 thru 2.3 for 2.4 we need to: - update the descriptive text in 4.3.2.7 of the Grid Modelling Guidelines - go through all the attribute tables in the Grid Modelling Guidelines and make the REQUIRED/OPTIONAL field match the LTDS profiles
2 | 2024-05-21 | open | Emil Hegyi, DIgSILENT E.Hegyi@digsilent.de | Emil to Bilal to Rose who forwarded to Pat, Chavdar, Alan | 2 - DIgSILENT BoundaryPoint attributes.docx | 2 - DIgSILENT BoundaryPoint attributes response.docx | 2024-07-10 Pat responded with 'have identified cause' email; 2024-07-29 Pat sent out 'it's fixed' email to attendees of July 12 Technical call with 2 - DIgSILENT BoundaryPoint attributes response.docx attached | - Manual fix to correct namespace on attributes in LTDS deviation profile RDFS. - Notify CIMConteXtor of erroneous namespace being put on attributes in deviation profile RDFS
3 | before 2024-05-28 | open | Behnam Feizifar, SSEN | Behnam to Rose who forwarded to Pat, Chavdar, Alan | The FOS states that "Grid Modelling includes from the 132kV network (EHV network in Scotland) down to the lower voltage busbars of primary substations. It also includes details of any interconnectors at lower voltages between primary substations needed to assess the capability of the higher voltage networks." Can I ask please if you can clarify more what Ofgem means by "interconnectors at lower voltages between primary substations needed to assess the capability of the higher voltage networks" | Sent the following to Rose: Rose: Finally getting around to responding to the ‘another question’ part of the email below. Here’s what I would tell you: The old, 2011 LTS Form of Statement said the following with respect to the scope of modelling to be provided: “…detailed information is provided for 132kV networks (EHV in Scotland) to the lower voltage busbars of primary substations but includes details of any interconnectors at lower voltages that are needed to assess the capability of the higher voltage networks. After numerous attempts to improve the specificity of this description, we fell back to the 2011 version because we could not arrive at a more concise definition that the DNOs were comfortable with. It is a description whose understanding seems to require a substantial amount of historic domain knowledge. None of the following are described or defined anywhere authoritative (not in the Grid Code Glossary & Definitions, the Balancing and Settling Codes, or in the Distribution Grid Code): • EHV • primary substation • interconnector (in the sense of ‘connections between substations’ which is what I believe it means in the LTDS statement) The Distribution Code has ‘Interconnector’ as an entry in its generator Energy Conversion Technology table. The Grid Code Glossary & Definitions refer to the BSC which defines interconnector as follows: An Interconnector is the apparatus used to transfer electricity to or from the GB Total System1 from or to an external system (i.e. an electricity network outside of Great Britain operated in another country). I’m not sure how I would suggest responding to Behnam Feizifar. The scope has not changed from the earlier scope. The description seems to me to be very fuzzy, but appears to make sense to the seasoned DNO folks. Maybe suggest that Behnam consult with his internal SSEN folks that have previously published LTDS data. Or maybe suggest that the question be brought up at the ENA’s CIM IOP working group (WG) meeting. Bilal Amjad (Bilal.Amjad@Northernpowergrid.com) is the Technical Lead for that group. Apologies for not being able to be more definitive. Pat | Confirm that Rose has communicated with Behnam
4 | 2024-06-18 | open | Emil Hegyi, DIgSILENT E.Hegyi@digsilent.de | Emil to Rose who forwarded to Pat, Chavdar, Alan | 4 - DIgSILENT LTDSnotdefined enumeration value attributes in RDFS.docx | 4 - DIgSILENT LTDSnotdefined enumeration value attributes in RDFS analysis.xlsx and 4 - DIgSILENT LTDSnotdefined enumeration value attributes in RDFS response.docx | 2024-07-10 Pat responded with 'have identified cause' email; 2024-07-29 Pat sent out 'it's fixed' email with 2 - DIgSILENT BoundaryPoint attributes response.docx attached | - Chavdar update his merging software to delete the ‘allowed value attributes’ of enumeration classes that appear in the deviation profiles. - Regenerate EQ, SC and SSH LTDS merged profile RDFS files and SHACL rules.
5 |  | open | André Schindler, DIgSILENT A.Schindler@digsilent.de | Andre to Bilal Amjad (Bilal.Amjad@Northernpowergrid.com) to Pat, Chavdar, Alan | 5 - DIgSILENT clarifications 2024-06-19.docx, as described in: - item 1 - Reverse flow capability of transformers - item 2 - Operational limits for switches - item 3 - Overlapping of date in OperationalLimitSet - item 4 - Equivalent branch elements for network reduction - item 5 - Unbalanced short-circuit calculation | 5 - DIgSILENT clarifications 2024-06-19 response.docx | 2024-07-01 Pat sent her answers; Chavdar to review | - update UML to add some description to the OperationalLimitSet.validFrom and .validTo attributes - update Grid Modelling Guidelines to explain use of .validFrom and .validTo in examples
6 |  | open | André Schindler, DIgSILENT A.Schindler@digsilent.de | André to Pat | 6 - DIgSILENT clarifications 2024-07-02, as described in: - item 1 - Limits for Switches - item 2 - EquivalentBranch - itme 3 - Short-Circuit Calculation | 6 - DIgSILENT clarifications 2024-07-02 response | 2024-07-09 Pat sent her answers; Chavdar to review; Authorised decision-making group to address item 2-EquivalentBranch | - in UML, remove EquivalentBranch from the LTDSnotDefined package in the Equipment deviation and ShortCircuit deviation profile packages - update Grid Modelling Guidelines to include example of use of EquivalentBranch for external model representation - consider adding a note regarding the use of EquivalentInjection and EquivalentBranch for interal anonimization
7 |  | open | Paul Thompson paul.js.thomson@nationalgrideso.com | GC0139 call | DNOs do not own SuperGrid transformer data and probably shouldn't be sharing it |  | Discuss with Ofgem | probably - update the Grid Modelling Guidelines to remove the SuperGrid Transformer from description of Transmission boundary modelling
8 |  | open | Emil Hegyi, DIgSILENT E.Hegyi@digsilent.de | Emil to Pat | For some of the line-models, our DNO customers are using line-containers to group line sections in their grid models. We plan to exchange these line-containers as CIM Line, while the line sections will be exchanged as CIM ACLineSegments. The problem we are facing is that PowerFactory does not provide support for storing geographic coordinates on line segments. This is only possible on the line container. Furthermore, for obvious reasons, it is not possible to distribute the coordinates from the line container to the line segments in the LTDS export process. We presume that the exchange of line coordinates is also possible via the CIM Line, as the Line is also a PowerSystemResource. In this constellation, however, no geocoordinates would be assigned to the ACLineSegments within the Line. LTDS is relatively strict in the sense, as it explicitly requires coordinates for all ACLineSegments: Source: https://www.ofgem.gov.uk/sites/default/files/2024-04/LTDS%20Grid%20Modelling%20Annex%201%20-%20Grid%20Modelling%20Guidelines.pdf, page 54 Would it be possible to moderate this requirement by also allowing the exchange of line geocoordinates in a Location associated with the Line instead of only in Location associated with the ACLineSegment? | Pat to Chavdar and Rose on 2024-07-29: I understand what Emil is saying, and wonder, Chavdar, if CGMES could give us a steer on this? So, a couple questions: 1. Is there is a data population/usage requirement in CGMES related to this? (I find the SHACL rule regarding PositionPoint being required and .mainAddress not being required, but nothing else in the CGMES_Constraints_Repository spreadsheet I have.) 2. What would a product conformant to CGMES v3.0 be expected to be able to handle in the way of incoming data? Would it have to be able to read and store a Location attached to every ConductingEquipment subtype? This question, Rose, is different from the earlier ones as it’s not a clarification or error identification, it’s a request to modify requirements due to vendor product tooling. It’s the sort of question that should be understood and evaluated pragmatically on the basis of its benefit to the mandated exchange solution (in this case LTDS). I’m dubious about benefit, but the context of conventional industry usage needs to be factored in to arrive at the best response. That’s why I’m asking the above question. In any event, Ofgem will need to be the official respondee in this case because of the nature of the request. I just want to be sure we present the full picture to you. Chavdar to Pat and Rose on 2024-07-30: I looked at this. Indeed I see what Emil is saying, and in CGMES there is no direct guidance on this. I do not recall that we specified requirements more than PowerSystemResource reference. Then vendors are free and it seems PowerFactory is giving the coordinated to the container as this somehow packages the set. I do not recall why we explicitly said ConductingEquipment. Maybe we meant that these classes should have coordinates, but the coordinates not necessarily attached to the conducting equipment ..... I guess this is another discussion point I assume in this situation we need to look at the business need. If we need to identify the coordinate of each line segment then we need vendors to support it if we only need to accurately describe the coordinates of a line, then coordinates on the container are the right thing to do. There is another angle to consider (a bit related to the semantics) - What is the drive to make a new ACLineSegment? For me a new segment happens if the characteristics of the line in terms of impedance change. If this is the case then we need to see if the DNOs follow that and then also clarify the GIS data These are all good interoperability questions that needs some discussion | Discuss with decision-making group | unknown at this time